## Slide 1: PRESSURE
JD
JULIO 2016

## Slide 2: BAROMETRIC PRESSURE:
A. - Barometric pressure
It is the weight of the air pressing on specific area and normally called atmosphere. It often is expressed in different units such as bar or milibar, kg/cm2, psi etc. In any case it is a force on a unit of area. This force also can be expressed by the height of some liquid such as mercury or water which then is mm or inches Hg (mercury), mm or inches WC (water column).
The height multiplied by the specific gravity of the liquid gives the height in water column. If that is expressed in mm the value is equal to pressure in kg/m2.
It is clear then, that the atmospheric pressure changes with altitude. The higher the location, the lower the weight of air that has to be supported by the surface, which means that the pressure is lower than it is on sea level.

## Slide 3: BAROMETRIC PRESSURE:
This relation is not linear and the pressure can be calculated by the following equation:
Psl: 760 mmHg
hsl: m

## Slide 4: PRESSURE VS ALTITUDE:

## Slide 5: Some cement plants at high altitude:
Cementos Andino (Peru) 4400 m
Sociedad Boliviana de Cemento (Bolivia) 4000 m
Cementos Paz del Rio (Colombia) 2560 m
Cementos Samper (Colombia) 3000 m
Exercise: calculate the barometric pressure at these plants
The average pressure at sea level is the “Normal pressure”, which is mostly expressed in mercury column (mm or inches).

## Slide 6: Exercise: calculate the height of the water column

## Slide 7: RELATIVE PRESSURE:
Relative pressure
That is the pressure inside a vessel, duct etc. The value shows the difference between the outside pressure and the pressure inside the vessel or duct.

## Slide 8: ABSOLUTE PRESSURE:
C. - Absolute pressure
The absolute pressure is the sum of the barometric pressure plus the relative pressure:
Pabs = Pbarometric + Prelative

## Slide 9: ABSOLUTE PRESSURE: EXAMPLE.
Example:
Stack closed at the top. Gas temperature: 1000 deg C Stack height:100 m
Gas: Air, normal ambient conditions.
Exercise:
Calculate the absolute and relative pressure at each measuring point

## Slide 10: ABSOLUTE PRESSURE: EXAMPLE.
Example: Preheater ID fan, Gas temp. 350 deg C, distance between “A” and “B”, 70 m. specific gravity of the gas 1.4 kg/Nm3.
Calculate the relative and absolute pressure at “A” and “B”

## Slide 11: STATIC PRESSURE:
D. - Static pressure:
All gases expand evenly in all directions. In a vessel where no movement is present, the pressure measured in any of its walls is the same. Because there is no movement, only static pressure is present.

## Slide 12: DYNAMIC PRESSURE:
E. - Velocity pressure or dynamic pressure:
Velocity pressure is produced by the gas movement and it is the kinetic energy produced by the moving gas stream. In our applications in the cement plant we have mostly moving gases. The velocity pressure can be calculated as follows
where the following symbols are used:
Vp = Velocity pressure (mm WC)
 = specific gravity (kg/m3)
g = gravity
The velocity pressure increases with the square of the velocity and proportional to the specific gravity.

## Slide 13: TOTAL PRESSURE:
F. - Total pressure
In a system with moving gases the total pressure is the sum of static pressure + velocity pressure
In a system without pressure losses the total pressure is constant.

## Slide 14: EXAMPLES AND EXCERCISES:
G. - Examples and exercises
Example:
Assumption no pressure losses
Ductwork at the fan outlet, static pressure 100 mm WC
Gas = Air under normal conditions.
Area 1 = 1 m2, area 2 = 0.5 m2
Gas volume: 1200 m3/h

## Slide 15: EXAMPLES AND EXCERCISES:
Example:
Draw the lines for static pressure and
the lines for velocity pressure

## Slide 16: EXAMPLES AND EXCERCISES:
Example:
Assumption no pressure losses
Ductwork at the fan outlet, static pressure 150 mm WC
Gas = Air under normal conditions.
Area 1 = 0.5 m2, area 2 = 1 m2
Gas volume: 1200 m3/h

## Slide 17: EXAMPLES AND EXCERCISES:
Example:
Draw the lines for static pressure and
the lines for velocity pressure

## Slide 18: EXAMPLES AND EXCERCISES:
Example:
Assumption a. - no pressure losses b. - with pressure loss
Ductwork at the fan inlet
Gas = Air under normal conditions.
Area 1 = 1 m2, area 2 = 0.5 m2
Gas volume: 1200 m3/h

## Slide 19: EXAMPLES AND EXCERCISES:
Example:
Draw the lines for static pressure and
the lines for velocity pressure

## Slide 20: EXAMPLES AND EXCERCISES:
Example:
Assumption a. - no pressure losses b. with pressure loss
Ductwork at the fan inlet
Gas = Air under normal conditions.
Area 1 = 0.5 m2, area 2 = 1 m2
Gas volume: 1200 m3/h

## Slide 21: EXAMPLES AND EXCERCISES:
Example:
Draw the lines for static pressure and
the lines for velocity pressure

## Slide 22: EXAMPLES AND EXCERCISES:
Duct on the fan outlet side, static pressure 200 mm WC
Gas: Air under normal conditions
No pressure losses
Fan static pressure 100 mm WC
Gas velocity: 10 m/s

## Slide 23: EXAMPLES AND EXCERCISES:
Draw the different height of water columne according to the indicated measurements.

## Slide 24: EXAMPLES AND EXCERCISES:
Duct on the fan inlet side
Gas: Air under normal conditions
No pressure losses
Gas velocity: 10 m/s

## Slide 25: EXAMPLES AND EXCERCISES:
Draw the different measurements in mm WC

## Slide 26: EXAMPLES AND EXCERCISES:
Ductwork connected to fan inlet
Area 1 = 1 m2, Area 2 = 0.5 m2, Area 3 = 2 m2
Gas: Air under normal conditions
Gas volume: 36,000 m3/h
No pressure loss

## Slide 27: EXAMPLES AND EXCERCISES:
Draw the different measurements in mm WC.

## Slide 28: EXAMPLES AND EXCERCISES:
Ductwork connected to fan outlet, static pressure 300 mm
Area 1 = 1 m2, Area 2 = 0.5 m2, Area 3 = 2 m2
Gas: Air under normal conditions
Gas volume: 36,000 m3/h
a. - No pressure loss
b. - With pressure loss

## Slide 29: EXAMPLES AND EXCERCISES:
Draw the lines for velocity pressure and static pressure

## Slide 30: EXAMPLES AND EXCERCISES:
Ductwork connected to fan inlet
Area 1 = 1 m2, Area 2 = 0.5 m2, Area 3 = 2 m2
Gas: Air under normal conditions
Gas volume: 36,000 m3/h
a. - No pressure loss
b. - With pressure loss

## Slide 31: EXAMPLES AND EXCERCISES:
Draw the graph for velocity pressure and static pressure

## Slide 32: EXAMPLES AND EXCERCISES:
On the suction side of the fan -100 mm WC is measured and
on the discharge side + 50 mm WC.
Indicate the velocity pressure and the total pressure if the volume flow is 24.000 m3/h,
The area at the inlet is 1.5 m2
The area at the outlet where the measurement is taken is 1.5 m2
No pressure losses are considered.

## Slide 33: EXAMPLES AND EXCERCISES:
On the suction side of the fan -100 mm WC is measured and
on the discharge side + 50 mm WC.
Indicate the velocity pressure and the total pressure if the volume flow is 24.000 m3/h.
The area at the inlet is 1.0 m2
The area at the outlet where the measurement is taken is 1.5 m2
No pressure losses are considered.

## Slide 34: EXAMPLES AND EXCERCISES:
On the suction side of the fan -50 mm WC is measured and
on the discharge side + 50 mm WC.
Volume flow is 30.000 m3/h,
Fan inlet and outlet area is 1.0 m2
The enlarged area is 2.0 m2
Draw the curve for static pressure and velocity pressure
a. - No pressure losses are considered.
b. - With pressure loss

## Slide 35: EXAMPLES AND EXCERCISES:
On the suction side of the fan -100 mm WC is measured and
on the discharge side + 50 mm WC.
Volume flow is 24.000 m3/h,
Fan inlet area = 1.0 m2
Fan outlet area = 1.0 m2
Enlarge area = 2.0 m2
a. - No pressure losses are considered.
b. - With pressure loss

## Slide 36: EXAMPLES AND EXCERCISES:
Inlet area 1 m3
F1 = 0.5 m2 F2 = 1.5 m2 F3 = 0.75 m2
F4 = 0.5 m2 F5 = 1.0 m2 F6 = 2.00 m2
Gas: Air under normal conditions
Gas volume: 72,000 m3/h
Fan pressure: 250 mm
a. - No pressure losses are considered
b. - With pressure loss

## Slide 37: EXAMPLES AND EXCERCISES:
Draw the curves for static pressure and velocity pressure